Citect for Windows

Driver Specification

DNIP

(Danfoss Net Interface Protocol)

- Driver version history

| Version | Date | Modified By | Details |
| --- | --- | --- | --- |
| 1.0.0.A1 | 2006-12-15 | Tomas Rook | Main development |
| 1.0.0.A2 | 2007-04-04 | Tomas Rook | Some updates |
| 1.0.0.A3 | 2007-04-18 | Tomas Rook | Writes etc |
| 1.0.0.A4 | 2007-04-26 | Tomas Rook | Bug fix, AS/DS determined from Status Flag |
| 1.0.0.B1 | 2007-05-15 | Tomas Rook | May write unread values (read-before-write) |
| 1.0.0.B2 | 2007-05-16 | Tomas Rook | Statistics updated, new parameters |
| 1.0.0.B3 | 2007-05-21 | Tomas Rook | Transaction number behaviour updated |
| 1.0.0.B4 | 2007-05-25 | Tomas Rook | New redundancy parameters added |
| 1.0.0 | 2007-05-30 | Tomas Rook | Relase (no updates) |
| 1.0.1 | 2007-09-25 | Tomas Rook | Updated Date/Time behaviour |
| 1.0.2 | 2008-05-21 | Tomas Rook | DanDuc scanlist read could cause answer mixup (PROM dependant features) |

- Driver documentation version history

| Date | Modified By | Details |
| --- | --- | --- |
| 2007-05-09 | Tomas Rook | Preliminary |
| 2007-05-16 | Tomas Rook | Added parameter DebugAlarms and WriteDigitalAsFF |
| 2007-05-21 | Tomas Rook | Added parameter PacketNumberRange. Stats updated. |
| 2007-05-28 | Tomas Rook | Added new parameters |
| 2008-05-21 | Tomas Rook | Updated driver version history |

Contents

1.	QA	6

1.1	Introduction	6

1.2	Procedure for generating a new driver	6

2.	Target Device(s) and Protocol	7

2.1	Introduction	7

2.2	Device Manufacturer	7

2.3	Device Definition	7

2.4	Communications Method	7

2.5	Communications/Hardware Configuration	7

2.5.1	GW-PC PC Cable	8

2.5.2	GW-UDP PC Cable	8

2.5.3	I/O Device Settings	9

2.5.4	Software Setup	9

2.6	Contacts	9

3.	Protocol Requirements	10

3.1	Introduction	10

3.2	Initialising the Port	10

3.3	IO Device Online Test	10

3.4	State Flow Description	10

3.5	Message Structure	10

3.6	Data Format	11

3.7	Checksum	11

3.8	Extended Protocol Description	11

3.9	Error Handling	11

3.10	Single reads	12

3.11	Scanlist reads	12

3.12	Scanlist addressing problems	12

3.13	Function Block reads	12

3.14	How to determine if Single Read is to be used	12

3.15	Request Performance	13

3.16	Writes	13

3.17	Differences between Citect DNIP driver and Master 2000	13

3.18	Citect Cache	14

3.19	DNIP.DBF	14

4.	User Interface	16

4.1	Introduction	16

4.2	Driver Name	16

4.3	Ports Form (COMX setup)	16

4.3.1	Baud Rate	16

4.3.2	Data Bits	16

4.3.3	Stop Bits	16

4.3.4	Parity	16

4.3.5	Special Opt	16

4.4	Ports Form (TCPIP setup)	16

4.4.1	Baud Rate	16

4.4.2	Data Bits	16

4.4.3	Stop Bits	16

4.4.4	Parity	17

4.4.5	Special Opt	17

4.5	IO Devices Form	17

4.5.1	Protocol	17

4.5.2	Address	17

4.6	Pulldown lists Help	17

4.7	IO Device Data Types and Formats	17

4.8	IO Device Function Blocks and their Parameters (DNIP.DBF)	17

4.9	PROTDIR.DBF	27

4.10	Parameters and INI options	27

4.10.1	Standard Parameters	27

4.10.2	Driver Specific Parameters	27

4.11	Driver Specific Errors	31

4.12	Driver Error Help	31

4.13	Debug Messages	31

4.14	Stats Special Counters	31

4.15	Hints and Tips	32

5.	Basic Testing	33

5.1	Introduction	33

5.2	Procedure	33

6.	Performance Testing	35

6.1	Introduction	35

6.2	Calculating the Blocking Constant – Not applicable	35

7.	References	36

7.1	References	36

# QA

## Introduction

This document follows the development of the new driver. It serves as a functional specification, design specification and test specification.

## Procedure for generating a new driver

The following check list defines the QA steps for generating a new driver. This procedure must be followed for drivers to be integrated into Citect.

|  | Description | Person | Date |
| --- | --- | --- | --- |
| 1 | This specification document is written. | TR | 03.11.12 |
| 2 | Specification reviewed and accepted by R&D department. |  | n/a |
| 3 | Driver coded. | TR | 06.12.15 |
| 4 | Code and specification reviewed and accepted by R&D department. |  | n/a |
| 5 | Testing with connection project, and performance test. | TR | 07.04.23 |
| 6 | Driver integrated into Citect source and built. |  | n/a |
| 7 | Documentation is written (HLP or MVB files) |  | n/a |
|  | At this checkpoint coding is done and the driver is available as a beta. |  |  |
| 8a | Full testing is carried out. | TR | 07.05.25 |
| 8b | Performance testing is carried out. | TR | 07.05.12 |
| 8c | Specification and documentation updated from testing/performance tests | TR | 07.05.28 |
|  | At this checkpoint the testing is complete. |  |  |
| 9a | Review for completeness by developer, tester, documentor and R&D staff |  | n/a |
| 9b | Add driver to install disks |  | n/a |
| 9c | Add driver to protocols database |  | n/a |
| 9d | Support notified of new driver for training purposes |  | n/a |
| 10 | Sales notified of new driver |  | n/a |
|  | The driver is now finished. |  |  |

The hand over of a driver requires that all the above steps are completed and checked off.

# Target Device(s) and Protocol

## Introduction

This section defines the types of I/O Devices that are targeted by this driver.

## Device Manufacturer

Danfoss System Control A/S (DSC)
Hørkær 12B
DK-2730 Herlev
Denmark
+45 42 841622

## Device Definition

DanDuc (Danfoss part #088G0500)
MPV (Danfoss part #088B0089.

Both models are old and not available.

These digital substations (DSS) are configurated and programmed by DSC and their partners for different building automation projects. They have a configurable number of I/O’s (digital input, analog input, analog output etc). The maximum is 64 I/O’s of a single type, and a total of about 128 I/O’s.

GW-PC version 2.10 (Danfoss part #088F3101)
GW-UDP (NetBiter from www.intellicom.se using updated Linux Kernel and a specific software).

These are concentrator units (gateways) for routing and packets conversion from the RS-485 DanBuss to the DNIP protocol using RS-232 or UDP.

## Communications Method

Serial RS-232 or UDP to GW-PC/UDP-GW. From GW-PC/UDP-GW to DanDuc / MPV’s the Danfoss DanBuss RS-485 is used.

## Communications/Hardware Configuration

The GW-PC is connected to the PC using the ‘PC-GW PC Cable’ directly to a RS-232 port.

The GW-UDP is connected to the PC either directly to a RS-232 port using ‘GW-UDP PC Cable’ or over ethernet.

The DanDuc’s / MPV’s are connected to the gateways using a multidrop bus topology (one pair, twisted, AWG24 or similar). The terminations are turned on at each end of the bus. If the cable length is to exceed 1200 m (AWG24), a DanBuss repeater has to be used. The GW-PC, GW-UDP and DanDuc / MPV uses 24 VAC, 50 Hz. The gateways may be located anywhere on the bus. See the GW-PC or GW-UDP manual for more detailed setup instructions.

### GW-PC PC Cable

Use cable Danfoss part #191F4403. The specification is as follows:

### GW-UDP PC Cable

Specification is as follows:

### I/O Device Settings

The DanBuss (RS-485) should be terminated, using the internal terminations, at each end according to the installation instructions for DanBuss.

See respective gateway configuration manual for hardware configuration.

### Software Setup

The gateway router lines should be set up as for a typical direct connected Danfoss Master 2000 system (standard configuration).

The DHC address used (typical 0:10) must be set up in CITECT.INI.

## Contacts

Driver Development	TroSoft AB, Tomas Rook	+46 8 532 57262
DanBuss specialist	Danfoss System Control, Rune Klitgaard	+45 42 841622
Project Managment	Beijer Electronics AB, Göran Månsson	+46 155 214990

# Protocol Requirements

## Introduction

This section documents all the requirements of the protocol itself.

## Initialising the Port

No special initialisation is necessary.

## IO Device Online Test

The drivers’ response to CTDRV_INIT_UNIT and CTDRV_STATUS_UNIT is to issue a ‘delete scanlist’ function with the scanlist parameter set to wildcard 0xFE (delete all scanlist belonging to my DHC address).

## Message Structure

The message structure has the following format (DNIP frame):

| DLE | SOF | control | packet number | Data (0-121 bytes) | CRC | DLE | EOF |
| --- | --- | --- | --- | --- | --- | --- | --- |

The frame may be up to 128 bytes wide.

| DLE | 0x10 |
| --- | --- |
| SOF | 0x1F |
| ACK (control option) | 0x06 |
| SAD (control option) | 0x02 |
| Packet number | 0x11-0xFF |
| Data | See description below |
| CRC | See description below |
| DLE | 0x10 |
| EOF | 0x17 |

Every DNIP frame (SAD type) that is sent has to be acknowledged. The acknowledge DNIP frame has no data part and has to have the same packet number as the frame it is to acknowledge.

The data part looks like:

| Datalen | The total length of the data part (excluding this byte) |
| --- | --- |
| Function code | Always 0x41 (MPV/DanDuc message) |
| Receiver address Low | The lower part (0-127) and the upper parts’ LSb. |
| Receiver address High | The upper part (0-127) right shifted one bit. The MSb’s is used to determine message priority. |
| Sender address Low | The lower part (0-127) and the upper parts’ LSb. |
| Sender address High | The upper part (0-127) right shifted one bit. The MSb’s is used to determine message priority. |
| Transaction # | Always zero |
| Command Type | Control/Sense/Event/Answer |
| Command | See extended description (could be FUNCTION_BLOCK, CLOCK, SYSTEM etc) |
| Count | The count of DNIP frames. If the following part isn’t enough to transport all data, then it is cut into two or more frames. This byte indicates which frame it is. If it has the MSb set, then it is the first frame. The other 7 bits indicate how many frames it is left. I.e. 0x80 indicates that this is the first frame, and it is zero frames left. 0x82 indicates that it is the first frame, and there is 2 frames left. 0x01 indicates that it is one frame left, and this frame is not the first one. |

The following part is optional and depends of the command. The way it looks like when it returns depends of the command.

| Type | Function block type, ex 0x02 is AI, 0x03 is AIB etc |
| --- | --- |
| Block | The block number, 0x00-0x1F, or 0xFF which means all function blocks |
| Parameter | The parameter, 0x00-0xFD, or 0xFF which means all parameters |

## Data Format

The data format i 8-bit ascii. Any character is valid in the data part, which means that the frame has to be DLE expanded before transmission. Upon reception, the extra DLE’s has to be removed.

The dataformat is exactly the same for serial and TCP/UDP transmissions (for serial communications an extra even parity bit should be applied by the OS).

## Checksum

The CRC (which not really is a Cyclic Redundancy Check) is calculated from the control character and to the last byte of the data part. For an acknowledge this means that the CRC is calculated from the control character and the packet number. The CRC is calculated before any DLE expanding is made. Even the CRC is DLE expanded if the CRC happens to be a DLE.

The actual calculation is made by XORing the CRC with all bytes inside the frame, including control character and packet number. The CRC begins with zero.

## Extended Protocol Description

The fully protocol description is found in three files available from Danfoss, MKS001-MKS003, which thorougly describes the DanBuss protocol (about 300 pages).

## Error Handling

2 consecutive packet timeouts will put the device off-line. The packets are acked by the receiving gateway. The gateway handle retries on the bus, i.e. the driver should not do this, hence Retrys is set to 0.

The on-line checking is made by a scanlist delete request. The device will return to the on-line state as soon as the driver gets any response from the device.General Driver description

## Single reads

This driver is of a hybrid ‘Front-End-Back-End’ type, and therefore has a cache list of variables that has been read by Citect as single reads.

The driver automatically will perform update requests when the variables in the cache list are old (determined by parameter setting). Cache objects are by default never deleted, they are just marked as obsolete when Citect has shown no interest within a specified time. When Citect request the value again, the cache object is reactivated and requested from using DNIP.

## Scanlist reads

The driver will create scanlists to increase performance when reading parameters. These lists are made up of the parameters Citect are trying to read. Though Citect is working asyncronously with a limited number of internal DCB requests (MaxPending) the driver will have to wait some time from the first request from Citect until it determines it is time to create a scanlist (or not if there are to few requests).

The time is setup using the ScanListFlushTime parameter (defaults to 80 ms).

Scanlists updates are automatically sent by the device when any of the requested parameters is changed (ex a temperature or digital input changes). All scanlists are also automatically sent by the device in a cyclic manner even if nothing has changed.

## Scanlist addressing problems

The device will reject scanlist creation if any of the requested parameters is out of range. The device will not report which parameter is out of range. Unfortenately Citect kernel will only report the first DCB address in the scanlist, which most likely not is the failing parameter.

To determine the exact address of the failing parameter, the Citect.INI parameter [DNIP]ForceSingleRead should be set to 1. It will cause all reads to be single reads.

This will severe degrade performance but will report the failing parameter.

The Trend and Alarm server could be turned off during debugging to ensure functionality.

The ForceSingleRead parameter could be set in a specific I/O Device section in Citect.INI and it is dynamically applied when Citect tries to restart a failing device (Citect does not need a restart, the IODeviceControl() function may be used).

## Function Block reads

Some parameters are often read in the same graphic as others belonging to the same function block, such as PIDREG, TIMCON etc. The P-variable most likely is to be read when the I-variable is read etc.

The driver will read the complete function block when Citect request the first parameter. These parameters are set as ‘Blocked Read’ in DNIP.DBF.

## How to determine if Single Read is to be used

The driver will by default try to create scanlists. But there are some occasions when scanlists are not wanted, these are:

- When we read parameters where we expect Citect to request more parameters from the same function blick, ex TIMCON, PIDREG etc. In this case the driver issue a single read requesting the complete function block.

- When we have requested just a few parameters from the device, then single reads are less bus intense than the scanlist create process (controlled by the ScanListTreshold parameter)

- When we are trying to write a value to the device and it has never been read. To write a new parameter value, we need not only the value itself (which comes from Citect), but also some flags associated with the value (storage format etc). Scanlist reads does not return all necessary flags, hence we need to read it from the device first as a single read before it is written. If we have access to PunktDB.DAT, the necessary flags could be collected from the database. The exact behaviour is determined by parameter settings in Citect.INI.

## Request Performance

The DNIP/Danbuss is a routing net protocol (though routing is not supported by this driver), which communicates with the maximum speed of 4800 bps (9600 bps at DNIP level).

Due to its complicated structure and packet overhead it has a generally bad performance.

Citect blocked reads will almost always decrease performance, and is turned off.

However, the driver will automatically group requests and create scanlists as described above. Medium time for a scanlist request is about 0,7-1,2 seconds.

This means that Citect always indicate a very high channel usage. The default is to handle 75 outstanding DCB’s at one time.

## Writes

Write requests can never be blocked. However, Citect may push a lot of write DCB’s to the same address if the user use a Slider etc to set the value, and let it use ‘Continous update of tag’. The driver will append all write request DCBs. When the driver decides to send the write request it will always use the last appended DCB.

All DCBs will get the same result code.

If the variable that is to be written do not exist in the cache object list, it will be added. The driver will first actually read the variable to fill in the parameter block structure, then the write will be performed and the write DCB is returned.

When a parameter is written, it will automatically be marked as obselete to force a fast re-read.

Writes requests always have highest priority.

## Differences between Citect DNIP driver and Master 2000

Some parameters presented on the Master 2000 SCADA is read from the database (function block/programming database, the Btrieve PunktDB.DAT) and not from the devices. A typical example is the TIMCON block, where most parameters will be presented from the PunktDB.DAT file. The reason is performance related.

This difference may cause irregularities between Citect and Master 2000 when comparing values between the SCADA systems.

Ex, if you change the start time of TIMCON prog 1 in Citect it will not be updated in Master 2000. If you change the start time of TIMCON prog 1 in Master 2000 it will be updated in Citect (could take some time, it will be updated when the CacheUpdateMax or CacheUpdateMin timers are passed).

The Citect DNIP driver will by default always read all parameters from the devices.

## Citect Cache

Citect do not need to do any cache, it will be handled by the driver.

## Redundancy

Citect redundancy is based upon the assumption devices may communicate with more than one master. This lead us to the conclusion the easiest way to achieve redundancy is to set both I/O Servers to different DHC-addresses.

This is also true if the gateway support this method (as the GW-UDP) and the devices have routerlines for double DHC addresses (ex 0:10-0:15).

However, the driver have some built-in functions for blocking traffic from one of the IOServers when there is a normal situation. The determination algorithm is based upon number of devices online. The determination process is applied per channel (port).

When any I/O Server is shutdown or fail in the keepalive process, the other server will initalize the devices and begin to communicate. This could take some time, though devices are per default offline on the standby/inactive IOServer.

Redundancy is handled by three threads not blocked by - nor blocking - the driver thread to prevent unwanted delays and lockups. The threads are: one server thread for incoming connection attempts, one client thread which will try to connect to the other I/O Server drivers server thread, and finally a supervisory thread that determines if the other I/O Server still is alive by sending keepalive packets cyclically.

Communication between the I/O Servers driver instances takes place over a TCP link. Only one link in each direction is created even if number of channels/ports are more than one.

If the driver built-in redundancy is used, then the scanlist number range must should be different on both I/O Servers to avoid conflicts.

Danfoss devices have poor performance and the necessity of redundancy should be taken under careful consideration.

## DNIP.DBF

The specification of a DanDuc contains 474 different variables. All these are defined in the DNIP.DBF. It has the following format:

TEMPLATE	UNIT_TYPE	RAW_TYPE	BIT WIDTH	LOW	HIGH	COMMENT

TIMCON%J%F.33	0x08215740	7	64	1	32	sOverrideOffStop

This row describes the TIMCON function block variable sOverrideOffStop, which is the variable that sets the end time for the ovveride time function for turning an output off. The variable is of a string type, 8 characters long (64 bits).

There may only be up to 32 function blocks of a type in a Danbuss device. However, the new devices contains more function blocks of the same type, and therefore new function block types are invented, such as AI and AIB, which means that AI1-32 is for analog input 1-32 and AIB1-32 is for analog input 33-64.

Block number is appended by Citect at compile time to form a complete address within the device.

Bit:  76543210765432107654321076543210

Desc: aaaaaaaaBBBBBBBBccccDDDeeeFFFFFF

00001000001000010101011101000000

0   8   2   1   5   7   4   0

aaaaaaaa	= (0-255)	BlockType

BBBBBBBB	= (0-255)	ParameterNumber

cccc	= (0-15) 	MPV parameter type

DDD	= (0-7)	Citect type

eee	= (0-7)	Control bits (SINGLEREAD / READFUNCTIONBLOCK)

FFFFFF	= (0-63)	BlockNumber

The UNIT_TYPE is used to specify the behaviour of the variable:

- The function block type

- The variable’s order in this function block (hex, it is equal to the last number in the template, 33)

5	The DANBUSS variable type, used internally for conversion.

typedef enum MPTypes {
	MP_MPBLOCKNAME,   /* = 18 byte */
	MP_AIPARAMETER,  /* = 8 byte */
	MP_DIPARAMETER,  /* = 6 byte */
	MP_AOPARAMETER,  /* = 5 byte */
	MP_DOPARAMETER,  /* = 3 byte */
	MP_ASPARAMETER,  /* = 3 byte */
	MP_DSPARAMETER,  /* = 2 byte */
	MP_PTRPARAMETER, /* = 4 byte */
	MP_DATPARAMETER,  /* = 2 byte */
	MP_UTCPARAMETER /* = 4 byte */
} MPTypes;

3	Citect’s type, is used to indicate any special format for time presentation etc.

typedef enum CITypes  {
CI_USERAW,	// Results in the raw format, no conversion is made
CI_UTCDATE,	// Results in date string, format 1997-11-21 from UTC
CI_UTCTIME,	// Results in time string, format 21:15 from UTC
CI_TIME	// Results in time string, format 21:15 from int
CI_STRWEEK	// Results in time string, format 4 21:15 from int (4=weekday)
} CITypes;

- Bit 0 = CONTROLBIT_SINGLEREAD
Bit 1 = Reserved
Bit 2 = CONTROLBIT_READFUNCTIONBLOCK

If bit 1 is set, it forces the driver to read this parameter as a single read (TIME/DATE etc)
If bit 2 is set, it indicates that this variable should be read in a function block blocked mode. It means that this variable will cause the driver to read the complete function block.

# User Interface

## Introduction

This section defines how the user will see the driver. This relates directly to how the Citect forms need to be filled out and any special INI options. For the kernel, the debug trace messages and the Stats.Special counters are documented.

## Driver Name

DNIP

## Ports Form (COMX setup)

### Baud Rate

9600 bps, or lower. The baudrate is set in the GW-PC, the default is 9600 bps.

### Data Bits

8

### Stop Bits

1

### Parity

Even (observe that this is an full 8 bit protocol using even parity, not 7 bits)

### Special Opt

-h	Windows will transmit data only when CTS is high.

-ti	Windows will raise RTS when there is enough room in the input buffer to receive incoming characters and drop RTS when there is not enough room in the input buffer.

-ri	Windows will raise DTR when there is enough room in the input buffer to receive incoming characters and drop DTR when there is not enough room in the input buffer.

## Ports Form (TCPIP setup)

### Baud Rate

n/a

### Data Bits

n/a

### Stop Bits

n/a

### Parity

n/a

### Special Opt

-i	The destination server IP-address, ex –i192.168.123.10.

-p	The destination server IP-port, ex –p10001.

-t	Use TCP/IP (default)

-u	Use UDP. When UDP is used, the target gateway (ex GW-UDP) need to be configured properly. When the driver is sending a request using UDP, the local source port will be randomly selected by the OS. The GW-UDP will always ack the DNIP packet to the local source port, but packets (answers) from the device itself will be routed using the router line settings in the GW-UDP and is sent to the destination port defined there. It will most likely not be the local source port.

-e	This parameter will cause the local source port to be the same as the destination server port (defined by –p), and should be used togheter with –u.

## IO Devices Form

### Protocol

DNIP

### Address

The address format looks like Net:Bus, ie 003:010 means Net 3, device 10. The address format is decimal. All devices connected to the samt physical Danbuss, must have the same net number.

It is however possible to have same net number for several gateways if the bus address of the devices are different, ex 10:1-10:3, 10:5-10:11 etc.

## Pulldown lists Help

The following entries should be included in the Citect Help.DBF spec file.

| TYPE | DATA | FILTER |
| --- | --- | --- |
| PROTOCOL | DNIP |  |

## IO Device Data Types and Formats

| IO Device Data Type | Valid Range | Citect Data Type | Description |
| --- | --- | --- | --- |
| String16 | 0x01 - 0xFF | STRING | Used for Function Block Names only (BLOCKNAME). Limited to 16 characters. If written, will only write to SRAM, EEPROM will not be updated (changes valid until next device boot). |
| Str24Hour | --:--, 00:00 – 24:00 | STRING | Used for Time Program (TIMCON Function Block). Presents the time in 24-hour clock format. |
| Str1WeekMinute | 1 00:00 - 7 24:00 | STRING | Used for Time Program (TIMCON Function Block). Presents the time in 24-hour clock format, and the day as 1-7 (Monday-Sunday). |
| StrUTCTime | 00:00 – 23:59 | STRING | Used for the device clock. Presents the time in 24-hour clock format. If the devices’ clock is written, it will be resynced by the GateWay within a minute (GW-PC). |
| StrUTCDate | YY-MM-DD | STRING | Used for the device clock. Presents the date in European (98.02.18) time/date format. If the devices’ clock is written, it will be resynced by the GateWay within a minute (GW-PC). |
| Float | -1024.00 - +1023.99 | REAL |  |
| Integer | -32768 - +32767 | INT |  |
| Boolean | 0 – 1 | DIGITAL |  |

## IO Device Function Blocks and their Parameters (DNIP.DBF)

| IO Device Type | DanBuss Function Block Parameter Name | DanBuss data type | Citect data type |
| --- | --- | --- | --- |
| AGATEn.0 | sBlockName | String16 | STRING |
| AGATEn.1 | fInput1 | Float | REAL |
| AGATEn.2 | fInput2 | Float | REAL |
| AGATEn.3 | fInput3 | Float | REAL |
| AGATEn.4 | fInput4 | Float | REAL |
| AGATEn.5 | fAmplific1 | Float | REAL |
| AGATEn.6 | fAmplific2 | Float | REAL |
| AGATEn.7 | fAmplific3 | Float | REAL |
| AGATEn.8 | fAmplific4 | Float | REAL |
| AGATEn.9 | fActualValue | Float | REAL |
| AGATEn.10 | iSelectCalcType | Integer | INTEGER |
| AGATEn.11 | bVisible | Boolean | DIGITAL |
| AGATEn.12 | bManuelMode | Boolean | DIGITAL |
| AIn.0 | sBlockName | String16 | STRING |
| AIn.1 | fMaxRange | Float | REAL |
| AIn.2 | fMinRange | Float | REAL |
| AIn.3 | fMaxLimit | Float | REAL |
| AIn.4 | fMinLimit | Float | REAL |
| AIn.5 | fAlarmOffset | Float | REAL |
| AIn.6 | bAlarmSend | Boolean | DIGITAL |
| AIn.7 | iAlarmDelay | Integer | INTEGER |
| AIn.8 | fOffset | Float | REAL |
| AIn.9 | fLockValue | Float | REAL |
| AIn.10 | bLockInput | Boolean | DIGITAL |
| AIn.11 | bSensorAlarm | Boolean | DIGITAL |
| AIn.12 | bAlarmMaxRange | Boolean | DIGITAL |
| AIn.13 | bAlarmMinRange | Boolean | DIGITAL |
| AIn.14 | bAlarmMaxLimit | Boolean | DIGITAL |
| AIn.15 | bAlarmMinLimit | Boolean | DIGITAL |
| AIn.16 | bCommonAlarm | Boolean | DIGITAL |
| AIn.17 | fActualValue | Float | REAL |
| AIn.18 | X1 | Integer | INTEGER |
| AIn.19 | Y1 | Integer | INTEGER |
| AIn.20 | X2 | Integer | INTEGER |
| AIn.21 | Y2 | Integer | INTEGER |
| AIn.22 | X3 | Integer | INTEGER |
| AIn.23 | Y3 | Integer | INTEGER |
| AIn.24 | X4 | Integer | INTEGER |
| AIn.25 | Y4 | Integer | INTEGER |
| AIn.26 | iTarget | Integer | INTEGER |
| AIn.27 | iFilter | Integer | INTEGER |
| AIn.28 | bMaxRangeAlarmEnable | Boolean | DIGITAL |
| AIn.29 | bMinRangeAlarmEnable | Boolean | DIGITAL |
| AIn.30 | bMaxLimitAlarmEnable | Boolean | DIGITAL |
| AIn.31 | bMinLimitAlarmEnable | Boolean | DIGITAL |
| AIn.32 | bSettingAlarmEnable | Boolean | DIGITAL |
| AIn.33 | bBusAlarmEnable | Boolean | DIGITAL |
| AIn.34 | iMPVAlarmGroup | Integer | INTEGER |
| AIn.35 | bVisible | Boolean | DIGITAL |
| AIn.36 | bManuelMode | Boolean | DIGITAL |
| AIBn.0 | sBlockName | String16 | STRING |
| AIBn.1 | fMaxRange | Float | REAL |
| AIBn.2 | fMinRange | Float | REAL |
| AIBn.3 | fMaxLimit | Float | REAL |
| AIBn.4 | fMinLimit | Float | REAL |
| AIBn.5 | fAlarmOffset | Float | REAL |
| AIBn.6 | bAlarmSend | Boolean | DIGITAL |
| AIBn.7 | iAlarmDelay | Integer | INTEGER |
| AIBn.8 | fOffset | Float | REAL |
| AIBn.9 | fLockValue | Float | REAL |
| AIBn.10 | bLockInput | Boolean | DIGITAL |
| AIBn.11 | bSensorAlarm | Boolean | DIGITAL |
| AIBn.12 | bAlarmMaxRange | Boolean | DIGITAL |
| AIBn.13 | bAlarmMinRange | Boolean | DIGITAL |
| AIBn.14 | bAlarmMaxLimit | Boolean | DIGITAL |
| AIBn.15 | bAlarmMinLimit | Boolean | DIGITAL |
| AIBn.16 | bCommonAlarm | Boolean | DIGITAL |
| AIBn.17 | fActualValue | Float | REAL |
| AIBn.18 | X1 | Integer | INTEGER |
| AIBn.19 | X1 | Integer | INTEGER |
| AIBn.20 | X2 | Integer | INTEGER |
| AIBn.21 | X1 | Integer | INTEGER |
| AIBn.22 | X3 | Integer | INTEGER |
| AIBn.23 | X1 | Integer | INTEGER |
| AIBn.24 | X4 | Integer | INTEGER |
| AIBn.25 | X1 | Integer | INTEGER |
| AIBn.26 | iTarget | Integer | INTEGER |
| AIBn.27 | iFilter | Integer | INTEGER |
| AIBn.28 | bMaxRangeAlarmEnable | Boolean | DIGITAL |
| AIBn.29 | bMinRangeAlarmEnable | Boolean | DIGITAL |
| AIBn.30 | bMaxLimitAlarmEnable | Boolean | DIGITAL |
| AIBn.31 | bMinLimitAlarmEnable | Boolean | DIGITAL |
| AIBn.32 | bSettingAlarmEnable | Boolean | DIGITAL |
| AIBn.33 | bBusAlarmEnable | Boolean | DIGITAL |
| AIBn.34 | iMPVAlarmGroup | Integer | INTEGER |
| AIBn.35 | bVisible | Boolean | DIGITAL |
| AIBn.36 | bManuelMode | Boolean | DIGITAL |
| AOn.0 | sBlockName | String16 | STRING |
| AOn.1 | fAnalogInput | Float | REAL |
| AOn.2 | fMaxRange | Float | REAL |
| AOn.3 | fMinRange | Float | REAL |
| AOn.4 | fMaxLimit | Float | REAL |
| AOn.5 | fMinLimit | Float | REAL |
| AOn.6 | fAlarmOffset | Float | REAL |
| AOn.7 | bAlarmSend | Boolean | DIGITAL |
| AOn.8 | iAlarmDelay | Integer | INTEGER |
| AOn.9 | fOffset | Float | REAL |
| AOn.10 | fLockValue | Float | REAL |
| AOn.11 | bLockInput | Boolean | DIGITAL |
| AOn.12 | fMaxOutValue | Float | REAL |
| AOn.13 | fMinOutValue | Float | REAL |
| AOn.14 | bOutputAlarm | Boolean | DIGITAL |
| AOn.15 | bAlarmMaxRange | Boolean | DIGITAL |
| AOn.16 | bAlarmMinRange | Boolean | DIGITAL |
| AOn.17 | bAlarmMaxLimit | Boolean | DIGITAL |
| AOn.18 | bAlarmMinLimit | Boolean | DIGITAL |
| AOn.19 | bCommonAlarm | Boolean | DIGITAL |
| AOn.20 | fActualValue | Float | REAL |
| AOn.21 | iFilter | Integer | INTEGER |
| AOn.22 | bMaxRangeAlarmEnable | Boolean | DIGITAL |
| AOn.23 | bMinRangeAlarmEnable | Boolean | DIGITAL |
| AOn.24 | bMaxLimitAlarmEnable | Boolean | DIGITAL |
| AOn.25 | bMinLimitAlarmEnable | Boolean | DIGITAL |
| AOn.26 | bSettingAlarmEnable | Boolean | DIGITAL |
| AOn.27 | bBusAlarmEnable | Boolean | DIGITAL |
| AOn.28 | iMPVAlarmGroup | Integer | INTEGER |
| AOn.29 | bVisible | Boolean | DIGITAL |
| AOn.30 | bManuelMode | Boolean | DIGITAL |
| ASMLn.0 | sBlockName | String16 | STRING |
| ASMLn.1 | fInput1 | Float | REAL |
| ASMLn.2 | fInput2 | Float | REAL |
| ASMLn.3 | fHysteres | Float | REAL |
| ASMLn.4 | bActualLevel | Boolean | DIGITAL |
| ASMLn.5 | bVisible | Boolean | DIGITAL |
| ASMLn.6 | bManuelMode | Boolean | DIGITAL |
| CTn.0 | sBlockName | String16 | STRING |
| CTn.1 | bCounterInput | Boolean | DIGITAL |
| CTn.2 | bStartStop | Boolean | DIGITAL |
| CTn.3 | iMeasureInterval | Integer | INTEGER |
| CTn.4 | iMultValue | Integer | INTEGER |
| CTn.5 | iDivideValue | Integer | INTEGER |
| CTn.6 | iPulseInterval | Integer | INTEGER |
| CTn.7 | bResetInput | Boolean | DIGITAL |
| CTn.8 | iMaxLimit | Integer | INTEGER |
| CTn.9 | bAlarmSend | Boolean | DIGITAL |
| CTn.10 | bPulseOutput | Boolean | DIGITAL |
| CTn.11 | bAlarmMaxRange | Boolean | DIGITAL |
| CTn.12 | bAlarmMinRange | Boolean | DIGITAL |
| CTn.13 | bAlarmMaxLimit | Boolean | DIGITAL |
| CTn.14 | bAlarmMinLimit | Boolean | DIGITAL |
| CTn.15 | bCommonAlarm | Boolean | DIGITAL |
| CTn.16 | fContValue | Float | REAL |
| CTn.17 | iAccumValue | Integer | INTEGER |
| CTn.18 | iTarget | Integer | INTEGER |
| CTn.19 | bTargetArea | Boolean | DIGITAL |
| CTn.20 | bMaxRangeAlarmEnable | Boolean | DIGITAL |
| CTn.21 | bMaxLimitAlarmEnable | Boolean | DIGITAL |
| CTn.22 | bSettingAlarmEnable | Boolean | DIGITAL |
| CTn.23 | bBusAlarmEnable | Boolean | DIGITAL |
| CTn.24 | iMPVAlarmGroup | Integer | INTEGER |
| CTn.25 | bVisible | Boolean | DIGITAL |
| CTn.26 | bManuelMode | Boolean | DIGITAL |
| DIn.0 | sBlockName | String16 | STRING |
| DIn.1 | bAlarmLevel | Boolean | DIGITAL |
| DIn.2 | iAlarmDelay | Integer | INTEGER |
| DIn.3 | bLockLevel | Boolean | DIGITAL |
| DIn.4 | bLockInput | Boolean | DIGITAL |
| DIn.5 | bAlarmSend | Boolean | DIGITAL |
| DIn.6 | bActualLevel | Boolean | DIGITAL |
| DIn.7 | bOutputAlarm | Boolean | DIGITAL |
| DIn.8 | iTarget | Integer | INTEGER |
| DIn.9 | bSettingAlarmEnable | Boolean | DIGITAL |
| DIn.10 | bBusAlarmEnable | Boolean | DIGITAL |
| DIn.11 | bSwitchOutput | Boolean | DIGITAL |
| DIn.12 | iMPVAlarmGroup | Integer | INTEGER |
| DIn.13 | bVisible | Boolean | DIGITAL |
| DIn.14 | bManuelMode | Boolean | DIGITAL |
| DIBn.0 | sBlockName | String16 | STRING |
| DIBn.1 | bAlarmLevel | Boolean | DIGITAL |
| DIBn.2 | iAlarmDelay | Integer | INTEGER |
| DIBn.3 | bLockLevel | Boolean | DIGITAL |
| DIBn.4 | bLockInput | Boolean | DIGITAL |
| DIBn.5 | bAlarmSend | Boolean | DIGITAL |
| DIBn.6 | bActualLevel | Boolean | DIGITAL |
| DIBn.7 | bOutputAlarm | Boolean | DIGITAL |
| DIBn.8 | iTarget | Integer | INTEGER |
| DIBn.9 | bSettingAlarmEnable | Boolean | DIGITAL |
| DIBn.10 | bBusAlarmEnable | Boolean | DIGITAL |
| DIBn.11 | bSwitchOutput | Boolean | DIGITAL |
| DIBn.12 | iMPVAlarmGroup | Integer | INTEGER |
| DIBn.13 | bVisible | Boolean | DIGITAL |
| DIBn.14 | bManuelMode | Boolean | DIGITAL |
| DLOGIKn.0 | sBlockName | String16 | STRING |
| DLOGIKn.1 | bInput1 | Boolean | DIGITAL |
| DLOGIKn.2 | bInput2 | Boolean | DIGITAL |
| DLOGIKn.3 | bInput3 | Boolean | DIGITAL |
| DLOGIKn.4 | bInput4 | Boolean | DIGITAL |
| DLOGIKn.5 | bActualLevel | Boolean | DIGITAL |
| DLOGIKn.6 | iSelectGateType | Integer | INTEGER |
| DLOGIKn.7 | bVisible | Boolean | DIGITAL |
| DLOGIKn.8 | bManuelMode | Boolean | DIGITAL |
| DLOGIKBn.0 | sBlockName | String16 | STRING |
| DLOGIKBn.1 | bInput1 | Boolean | DIGITAL |
| DLOGIKBn.2 | bInput2 | Boolean | DIGITAL |
| DLOGIKBn.3 | bInput3 | Boolean | DIGITAL |
| DLOGIKBn.4 | bInput4 | Boolean | DIGITAL |
| DLOGIKBn.5 | bActualLevel | Boolean | DIGITAL |
| DLOGIKBn.6 | iSelectGateType | Integer | INTEGER |
| DLOGIKBn.7 | bVisible | Boolean | DIGITAL |
| DLOGIKBn.8 | bManuelMode | Boolean | DIGITAL |
| DOn.0 | sBlockName | String16 | STRING |
| DOn.1 | bDigitalInput | Boolean | DIGITAL |
| DOn.2 | bAlarmLevel | Boolean | DIGITAL |
| DOn.3 | iAlarmDelay | Integer | INTEGER |
| DOn.4 | bLockLevel | Boolean | DIGITAL |
| DOn.5 | bLockInput | Boolean | DIGITAL |
| DOn.6 | bAlarmSend | Boolean | DIGITAL |
| DOn.7 | bActualLevel | Boolean | DIGITAL |
| DOn.8 | bOutputAlarm | Boolean | DIGITAL |
| DOn.9 | bSettingAlarmEnable | Boolean | DIGITAL |
| DOn.10 | bBusAlarmEnable | Boolean | DIGITAL |
| DOn.11 | iMPVAlarmGroup | Integer | INTEGER |
| DOn.12 | bVisible | Boolean | DIGITAL |
| DOn.13 | bManuelMode | Boolean | DIGITAL |
| FFn.0 | sBlockName | String16 | STRING |
| FFn.1 | bPresetInput | Boolean | DIGITAL |
| FFn.2 | bJInput | Boolean | DIGITAL |
| FFn.3 | bClockInput | Boolean | DIGITAL |
| FFn.4 | bKInput | Boolean | DIGITAL |
| FFn.5 | bResetInput | Boolean | DIGITAL |
| FFn.6 | bQOutput | Boolean | DIGITAL |
| FFn.7 | bQOutputInverted | Boolean | DIGITAL |
| FFn.8 | bVisible | Boolean | DIGITAL |
| FFn.9 | bManuelMode | Boolean | DIGITAL |
| FORSn.0 | sBlockName | String16 | STRING |
| FORSn.1 | bDigitalInput | Boolean | DIGITAL |
| FORSn.2 | iDelayTOn | Integer | INTEGER |
| FORSn.3 | iDelayTOff | Integer | INTEGER |
| FORSn.4 | bActualLevel | Boolean | DIGITAL |
| FORSn.5 | bVisible | Boolean | DIGITAL |
| FORSn.6 | bManuelMode | Boolean | DIGITAL |
| INTEGn.0 | sBlockName | String16 | STRING |
| INTEGn.1 | fAnalogInput | Float | REAL |
| INTEGn.2 | bStart | Boolean | DIGITAL |
| INTEGn.3 | bTurnInput | Boolean | DIGITAL |
| INTEGn.4 | fDivideValue | Float | REAL |
| INTEGn.5 | iSampleTime | Integer | INTEGER |
| INTEGn.6 | bResetInput | Boolean | DIGITAL |
| INTEGn.7 | fMaxLimit | Float | REAL |
| INTEGn.8 | bAlarmSend | Boolean | DIGITAL |
| INTEGn.9 | bAlarmMaxRange | Boolean | DIGITAL |
| INTEGn.10 | bAlarmMinRange | Boolean | DIGITAL |
| INTEGn.11 | bAlarmMaxLimit | Boolean | DIGITAL |
| INTEGn.12 | bAlarmMinLimit | Boolean | DIGITAL |
| INTEGn.13 | bCommonAlarm | Boolean | DIGITAL |
| INTEGn.14 | fActualValue | Float | REAL |
| INTEGn.15 | iSample | Integer | INTEGER |
| INTEGn.16 | bMaxRangeAlarmEnable | Boolean | DIGITAL |
| INTEGn.17 | bMaxLimitAlarmEnable | Boolean | DIGITAL |
| INTEGn.18 | bSettingAlarmEnable | Boolean | DIGITAL |
| INTEGn.19 | bBusAlarmEnable | Boolean | DIGITAL |
| INTEGn.20 | iMPVAlarmGroup | Integer | INTEGER |
| INTEGn.21 | bVisible | Boolean | DIGITAL |
| INTEGn.22 | bManuelMode | Boolean | DIGITAL |
| KOMPENn.0 | sBlockName | String16 | STRING |
| KOMPENn.1 | fOut1 | Float | REAL |
| KOMPENn.2 | fFlow1 | Float | REAL |
| KOMPENn.3 | fOut2 | Float | REAL |
| KOMPENn.4 | fFlow2 | Float | REAL |
| KOMPENn.5 | fOut3 | Float | REAL |
| KOMPENn.6 | fFlow3 | Float | REAL |
| KOMPENn.7 | fOutSensor | Float | REAL |
| KOMPENn.8 | fNightSetback | Float | REAL |
| KOMPENn.9 | bSetPointSwitch | Boolean | DIGITAL |
| KOMPENn.10 | bMinMaxLimiter | Boolean | DIGITAL |
| KOMPENn.11 | fLimiterAmplific | Float | REAL |
| KOMPENn.12 | fReturnSetPoint | Float | REAL |
| KOMPENn.13 | fReturnSensor | Float | REAL |
| KOMPENn.14 | fCompen | Float | REAL |
| KOMPENn.15 | fMinLimiter | Float | REAL |
| KOMPENn.16 | fMaxLimiter | Float | REAL |
| KOMPENn.17 | fFlowSensor | Float | REAL |
| KOMPENn.18 | fDeadBand | Float | REAL |
| KOMPENn.19 | bStopITime | Boolean | DIGITAL |
| KOMPENn.20 | fPBand | Float | REAL |
| KOMPENn.21 | iITime | Integer | INTEGER |
| KOMPENn.22 | bOverride_100 | Boolean | DIGITAL |
| KOMPENn.23 | bOverride_0 | Boolean | DIGITAL |
| KOMPENn.24 | bOpenOutput | Boolean | DIGITAL |
| KOMPENn.25 | bCloseOutput | Boolean | DIGITAL |
| KOMPENn.26 | fActualValue | Float | REAL |
| KOMPENn.27 | fCalcSetPoint | Float | REAL |
| KOMPENn.28 | bSwitchOutput | Boolean | DIGITAL |
| KOMPENn.29 | bVisible | Boolean | DIGITAL |
| KOMPENn.30 | bManuelMode | Boolean | DIGITAL |
| MATn.0 | sBlockName | String16 | STRING |
| MATn.1 | fAnalogInput | Float | REAL |
| MATn.2 | fOutputOffset | Float | REAL |
| MATn.3 | fActualValue | Float | REAL |
| MATn.4 | X1 | Integer | INTEGER |
| MATn.5 | Y1 | Integer | INTEGER |
| MATn.6 | X2 | Integer | INTEGER |
| MATn.7 | Y2 | Integer | INTEGER |
| MATn.8 | X3 | Integer | INTEGER |
| MATn.9 | Y3 | Integer | INTEGER |
| MATn.10 | X4 | Integer | INTEGER |
| MATn.11 | Y4 | Integer | INTEGER |
| MATn.12 | X5 | Integer | INTEGER |
| MATn.13 | Y5 | Integer | INTEGER |
| MATn.14 | X6 | Integer | INTEGER |
| MATn.15 | Y6 | Integer | INTEGER |
| MATn.16 | bVisible | Boolean | DIGITAL |
| MATn.17 | bManuelMode | Boolean | DIGITAL |
| OMRINDn.0 | sBlockName | String16 | STRING |
| OMRINDn.1 | fAnalogInput | Float | REAL |
| OMRINDn.2 | fMinLimit | Float | REAL |
| OMRINDn.3 | fMaxLimit | Float | REAL |
| OMRINDn.4 | bMinRange | Boolean | DIGITAL |
| OMRINDn.5 | bLimitRange | Boolean | DIGITAL |
| OMRINDn.6 | bMaxRange | Boolean | DIGITAL |
| OMRINDn.7 | bVisible | Boolean | DIGITAL |
| OMRINDn.8 | bManuelMode | Boolean | DIGITAL |
| OMSKFTn.0 | sBlockName | String16 | STRING |
| OMSKFTn.1 | fInput1 | Float | REAL |
| OMSKFTn.2 | fInput2 | Float | REAL |
| OMSKFTn.3 | bSwitchInput | Boolean | DIGITAL |
| OMSKFTn.4 | fActualValue | Float | REAL |
| OMSKFTn.5 | bVisible | Boolean | DIGITAL |
| OMSKFTn.6 | bManuelMode | Boolean | DIGITAL |
| OPTCONn.0 | sBlockName | String16 | STRING |
| OPTCONn.1 | bSwitchValue | Boolean | DIGITAL |
| OPTCONn.2 | fOutSensor | Float | REAL |
| OPTCONn.3 | fRoomSensor | Float | REAL |
| OPTCONn.4 | bSensorActive | Boolean | DIGITAL |
| OPTCONn.5 | fSetPoint | Float | REAL |
| OPTCONn.6 | fMaxSetPoint | Float | REAL |
| OPTCONn.7 | iTOn | Integer | INTEGER |
| OPTCONn.8 | iTOff | Integer | INTEGER |
| OPTCONn.9 | iMaxTOn | Integer | INTEGER |
| OPTCONn.10 | iMaxTOff | Integer | INTEGER |
| OPTCONn.11 | fSwitchTime | Float | REAL |
| OPTCONn.12 | bIDEActive | Boolean | DIGITAL |
| OPTCONn.13 | fEDESetPoint | Float | REAL |
| OPTCONn.14 | bDayLevel | Boolean | DIGITAL |
| OPTCONn.15 | bBoostLevel | Boolean | DIGITAL |
| OPTCONn.16 | bEDELevel | Boolean | DIGITAL |
| OPTCONn.17 | bIDELevel | Boolean | DIGITAL |
| OPTCONn.18 | bAlarmStart | Boolean | DIGITAL |
| OPTCONn.19 | bAlarmStop | Boolean | DIGITAL |
| OPTCONn.20 | fAlarmValue | Float | REAL |
| OPTCONn.21 | iCalcTOn | Integer | INTEGER |
| OPTCONn.22 | iCalcTOff | Integer | INTEGER |
| OPTCONn.23 | bVisible | Boolean | DIGITAL |
| OPTCONn.24 | bManuelMode | Boolean | DIGITAL |
| PIDREGn.0 | sBlockName | String16 | STRING |
| PIDREGn.1 | fSensorInput | Float | REAL |
| PIDREGn.2 | fCompen | Float | REAL |
| PIDREGn.3 | bSetPointSwitch | Boolean | DIGITAL |
| PIDREGn.4 | fDaySetPoint | Float | REAL |
| PIDREGn.5 | fNightSetPoint | Float | REAL |
| PIDREGn.6 | fMinLimit | Float | REAL |
| PIDREGn.7 | fMaxLimit | Float | REAL |
| PIDREGn.8 | fPBand | Float | REAL |
| PIDREGn.9 | iITime | Integer | INTEGER |
| PIDREGn.10 | iDTime | Integer | INTEGER |
| PIDREGn.11 | bLockITime | Boolean | DIGITAL |
| PIDREGn.12 | fOutputOffset | Float | REAL |
| PIDREGn.13 | fActualValue | Float | REAL |
| PIDREGn.14 | fCalcSetPoint | Float | REAL |
| PIDREGn.15 | fPIOutput | Float | REAL |
| PIDREGn.16 | bSwitchOutput | Boolean | DIGITAL |
| PIDREGn.17 | bVisible | Boolean | DIGITAL |
| PIDREGn.18 | bManuelMode | Boolean | DIGITAL |
| PREGn.0 | sBlockName | String16 | STRING |
| PREGn.1 | fSensorInput | Float | REAL |
| PREGn.2 | fCompen1 | Float | REAL |
| PREGn.3 | fCompen2 | Float | REAL |
| PREGn.4 | bSetPointSwitch | Boolean | DIGITAL |
| PREGn.5 | fAmplific1 | Float | REAL |
| PREGn.6 | fAmplific2 | Float | REAL |
| PREGn.7 | fSetPoint1 | Float | REAL |
| PREGn.8 | fSetPoint2 | Float | REAL |
| PREGn.9 | fMinLimit | Float | REAL |
| PREGn.10 | fMaxLimit | Float | REAL |
| PREGn.11 | fPFactor | Float | REAL |
| PREGn.12 | fDaySetPoint | Float | REAL |
| PREGn.13 | fNightSetPoint | Float | REAL |
| PREGn.14 | fOutputOffset | Float | REAL |
| PREGn.15 | fActualValue | Float | REAL |
| PREGn.16 | fCalcSetPoint | Float | REAL |
| PREGn.17 | fFilter | Float | REAL |
| PREGn.18 | bVisible | Boolean | DIGITAL |
| PREGn.19 | bManuelMode | Boolean | DIGITAL |
| PROPBn.0 | sBlockName | String16 | STRING |
| PROPBn.1 | fAnalogInput | Float | REAL |
| PROPBn.2 | fLowerSetPoint | Float | REAL |
| PROPBn.3 | fUpperSetPoint | Float | REAL |
| PROPBn.4 | fLowerAmplific | Float | REAL |
| PROPBn.5 | fUpperAmplific | Float | REAL |
| PROPBn.6 | fLowerLimit | Float | REAL |
| PROPBn.7 | fUpperLimit | Float | REAL |
| PROPBn.8 | fOutputOffset | Float | REAL |
| PROPBn.9 | fActualValue | Float | REAL |
| PROPBn.10 | bVisible | Boolean | DIGITAL |
| PROPBn.11 | bManuelMode | Boolean | DIGITAL |
| TIMCONn.0 | sBlockName | String16 | STRING |
| TIMCONn.1 | bOverrideDay | Boolean | DIGITAL |
| TIMCONn.2 | bOverrideNight | Boolean | DIGITAL |
| TIMCONn.3 | bActualLevel | Boolean | DIGITAL |
| TIMCONn.4 | fSwitchTime | Float | REAL |
| TIMCONn.5 | fActualTime | Float | REAL |
| TIMCONn.6 | sProg1Per1Start | Str24Hour | STRING |
| TIMCONn.7 | sProg1Per1Stop | Str24Hour | STRING |
| TIMCONn.8 | sProg1Per2Start | Str24Hour | STRING |
| TIMCONn.9 | sProg1Per2Stop | Str24Hour | STRING |
| TIMCONn.10 | sProg1Per3Start | Str24Hour | STRING |
| TIMCONn.11 | sProg1Per3Stop | Str24Hour | STRING |
| TIMCONn.12 | sProg2Per1Start | Str24Hour | STRING |
| TIMCONn.13 | sProg2Per1Stop | Str24Hour | STRING |
| TIMCONn.14 | sProg2Per2Start | Str24Hour | STRING |
| TIMCONn.15 | sProg2Per2Stop | Str24Hour | STRING |
| TIMCONn.16 | sProg2Per3Start | Str24Hour | STRING |
| TIMCONn.17 | sProg2Per3Stop | Str24Hour | STRING |
| TIMCONn.18 | sProg3Per1Start | Str24Hour | STRING |
| TIMCONn.19 | sProg3Per1Stop | Str24Hour | STRING |
| TIMCONn.20 | sProg3Per2Start | Str24Hour | STRING |
| TIMCONn.21 | sProg3Per2Stop | Str24Hour | STRING |
| TIMCONn.22 | sProg3Per3Start | Str24Hour | STRING |
| TIMCONn.23 | sProg3Per3Stop | Str24Hour | STRING |
| TIMCONn.24 | sProg4Per1Start | Str24Hour | STRING |
| TIMCONn.25 | sProg4Per1Stop | Str24Hour | STRING |
| TIMCONn.26 | sProg4Per2Start | Str24Hour | STRING |
| TIMCONn.27 | sProg4Per2Stop | Str24Hour | STRING |
| TIMCONn.28 | sProg4Per3Start | Str24Hour | STRING |
| TIMCONn.29 | sProg4Per3Stop | Str24Hour | STRING |
| TIMCONn.30 | sOverrideOnStart | Str1WeekMinute | STRING |
| TIMCONn.31 | sOverrideOnStop | Str1WeekMinute | STRING |
| TIMCONn.32 | sOverrideOffStart | Str1WeekMinute | STRING |
| TIMCONn.33 | sOverrideOffStop | Str1WeekMinute | STRING |
| TIMCONn.34 | iProgSelMonday | Integer | INTEGER |
| TIMCONn.35 | iProgSelTuesday | Integer | INTEGER |
| TIMCONn.36 | iProgSelWednesday | Integer | INTEGER |
| TIMCONn.37 | iProgSelThusday | Integer | INTEGER |
| TIMCONn.38 | iProgSelFriday | Integer | INTEGER |
| TIMCONn.39 | iProgSelSaturday | Integer | INTEGER |
| TIMCONn.40 | iProgSelSunday | Integer | INTEGER |
| TIMCONn.41 | bVisible | Boolean | DIGITAL |
| TIMCONn.42 | bManuelMode | Boolean | DIGITAL |
| TIMERn.0 | sBlockName | String16 | STRING |
| TIMERn.1 | bStartInput | Boolean | DIGITAL |
| TIMERn.2 | bStopInput | Boolean | DIGITAL |
| TIMERn.3 | bResetInput | Boolean | DIGITAL |
| TIMERn.4 | iMaxLimit | Integer | INTEGER |
| TIMERn.5 | bAlarmSend | Boolean | DIGITAL |
| TIMERn.6 | bAlarmMaxRange | Boolean | DIGITAL |
| TIMERn.7 | bAlarmMinRange | Boolean | DIGITAL |
| TIMERn.8 | bAlarmMaxLimit | Boolean | DIGITAL |
| TIMERn.9 | bAlarmMinLimit | Boolean | DIGITAL |
| TIMERn.10 | bCommonAlarm | Boolean | DIGITAL |
| TIMERn.11 | iActualValue | Integer | INTEGER |
| TIMERn.12 | iSelectTimerUnit | Integer | INTEGER |
| TIMERn.13 | bMaxRangeAlarmEnable | Boolean | DIGITAL |
| TIMERn.14 | bMaxLimitAlarmEnable | Boolean | DIGITAL |
| TIMERn.15 | bSettingAlarmEnable | Boolean | DIGITAL |
| TIMERn.16 | bBusAlarmEnable | Boolean | DIGITAL |
| TIMERn.17 | iMPVAlarmGroup | Integer | INTEGER |
| TIMERn.18 | bVisible | Boolean | DIGITAL |
| TIMERn.19 | bManuelMode | Boolean | DIGITAL |
| TRINDn.0 | sBlockName | String16 | STRING |
| TRINDn.1 | fAnalogInput | Float | REAL |
| TRINDn.2 | fMaxInValue | Float | REAL |
| TRINDn.3 | fMinInValue | Float | REAL |
| TRINDn.4 | fMaxOutValue | Float | REAL |
| TRINDn.5 | fMinOutValue | Float | REAL |
| TRINDn.6 | bMinOverride | Boolean | DIGITAL |
| TRINDn.7 | bMaxOverride | Boolean | DIGITAL |
| TRINDn.8 | bOverride_0 | Boolean | DIGITAL |
| TRINDn.9 | bOverride_100 | Boolean | DIGITAL |
| TRINDn.10 | bTurnOutput | Boolean | DIGITAL |
| TRINDn.11 | fActualValue | Float | REAL |
| TRINDn.12 | bVisible | Boolean | DIGITAL |
| TRINDn.13 | bManuelMode | Boolean | DIGITAL |
| DATE | sDate | StrUTCDate | STRING |
| TIME | sTime | StrUTCTime | STRING |

Where:

| n | The Function Block number. This can span from 1 to 32 for all types of function blocks. |  |
| --- | --- | --- |

Note: String16 has always a maximum length of 16 bytes.

## PROTDIR.DBF

| TAG | FILE | BIT_BLOCK | MAX_LENGTH | OPTIONS |
| --- | --- | --- | --- | --- |
| DNIP | DNIP | 16 | 256 | 0x0B47 |

## Parameters and INI options

### Standard Parameters

Block	16		(Citect blocking is prohibited)
Delay	20	ms
MaxPending 	75
Polltime	0	ms
Timeout	10000	ms
Retry	0		(Sets the complete packet retries, should be 0)
WatchTime	30	s

### Driver Specific Parameters

All DANBUSS specific parameters are located in the section ‘DanBuss’

| PARAMETER | DEFAULT | DESCRIPTION |
| --- | --- | --- |
| Delay | 20 ms | mecs between each packet sent to the gateway. This is not the bus access time (can’t be set by the driver). Multiple packets can not be outstanding for a single device, however MaxOutstandingPerChannel determines how many packets a gateway may handle. |
| TimeOut | 10000 ms | Timeout for a complete response from the device |
| Retrys | 0 | Number of retries made for a request to a specific device. The gateway handles retries on the bus, hence this should always be 0. |
| MaxPending | 75 | Number of DCBs the driver may handle simultanously. Actually the default is quite low for this driver, but Citect is not capable of handling an unlimited number of outstanding DCBs. This number must be multiplied by number of channels to get the total DCBs for Citect. |
| WatchTime | 30 s | When Citect send DCB requests to the driver, it have to respond within this time. This is also the cycle time for init and status requests for offline devices. It should be considerable high (preferrably higher than the default), though device restarts performed on still offline devices will slow down communication. |
| ConnectTimeout | 15000 ms | msecs we will let elapse until we consider the IP connect/reconnect failed. The IP layer may have an unreasonable timeout up to 120 seconds. |
| SleepAtShutDown |  |  |
| PacketTimeout | 2000 ms | mecs until we consider that the gateways did not receive our packet. |
| PacketRetries | 2 | Number of retries made when sending a packet to the gateway. If we does not get any ack then we consider the device to be offline (actually the complete channel is offline). If we have delays on the IP-layer and packets arrive in a burst, consecutive packets with the same packet number are always filtered. |
| IgnoreStartupErrors | 0 | If set to 1, irregularities in the variable database compared to the PunktDB.DAT file (if it is used), will not be reported. However, the parameters will be set as bad values if requested by Citect. Default is that the driver reports any potential problem at startup time using a messagebox. The messagebox will however block the startup sequence. |
| SleepAtShutDown | 1000 ms | When shutting down Citect, the driver will automatically send a packet to each devices causing any scanlists to be removed. Citect will immediately close the socket or COM-port when the driver returns from the shutdown procedure, causing the packets to be removed if they are not already sent (which is not lilkely). This small pause will allow all packets to be sent. If scanlists are not deleted from the device, they could cause the gateway buffers to be filled and could cause severe problems. |
| ForceSingleRead1 | 0 | If set to 1, it will cause the driver to issue single read requests. It will never create scanlists. This is necessary when trying |
| ShowAlarmEvents | 0 | If set to 1, it will cause the driver to echo all alarm events to Kernel. |
| DebugPacketAcks | 0 | If set to 1, it will cause the driver to show also packet acks when debugging is used in Kernel. These packet are of very little or no interest (if the gateway is allright). |
| TraceToLogFile | 0 | If set to 1, it will cause the driver to fill the file C:\DNIP.LOG with information of each call made in the driver. It will degrade performance and no check is made to ensure disk is not filled by the log file. |
| TestProtocolMode | 0 | If set to 1, it will cause the driver to use the internal test protocol instead of DNIP. Due to complicated structures in DNIP, the driver structures for scanlist, single reads and writes, was developed using an ASCII based PLC simulation software communicating using an in-house protocol. This mode is for internal structure testing purposes only. |
| CleanupTime | 1000 ms | msecs between each cleanup cycle. The cleanup cycle will determine when to refresh or delete scanlists and single read values. This parameter should not be altered. |
| DebugVerbose | 0 | If set to 1, it will cause the driver to write detailed information about each DNIP packet. Due to llimitations in Kernel not all information will be viewed, however it will be stored in SysLog.DAT for later analysis. |
| DebugAlarms | 1 | If set to 1, the driver will write alarm messages into Kernel main window (only when debugging is enabled in Kernel). |
| DisableWrite | 0 | If set to 1, it will cause the driver to always reject write requests. The failed write will be viewed in Kernel. |
| PreventStreamingWrites | 1 | If set to 1, it will cause the driver to filter write requests and always use only the last requests (if many write requests are made to the same parameter). |
| RequestTime | 20 ms | msecs for request cycle cleanups. Each cycle, the driver will scan through internal queues for work to do (create scanlists, move queues if the bus is free, create DNIP packets, update statistics, cleanup memory etc). |
| PunktDBPath |  | Path to the Btrieve PunktDB.DAT file. This file contains all function block programming in all devices. |
| ValidateAddressBehaviour | 2 | Determines how we should use the Btrieve PunktDB.DAT file. 0 Driver is not using PunktDB.DAT at all 1 Driver will validate addresses at startup time (all addresses in the variable dbf will be validated even if they are not used) 2 Driver will validate address as they are used. The validation process will only take place once even if Citect requests the parameter multiple times. The driver will dynamically re-validate the address if PunktDB.DAT is updated (timestamp changes). This setting may cause performance to be degraded, at least when parameters are read first time. 3 The driver will only use PunktDB.DAT to fill parameter structures for write requests. |
| DHCAddress | 0:10 | Master address of the driver. This must match router line settings in gateways, and it should not be mixed with ex Master 2000 or MPVT/M100 settings. If the DNIP driver built-in redundancy is to be used, DHCAddress should be equal on both servers. If the Citect redundancy is to be used, this address must differ on both servers. |
| MaxOutstandingPerChannel | 4 | Number of outstanding packets the gateways will accept for each channel. Only one outstanding packet per device is allowed and it is not configurable. For a GW-PC this should be set to 2. |
| CacheLiveTime | 0 ms | msecs until a cache object is deleted (single reads and writes). If set to 0, cache objects are never deleted. It is better leaving cache objects in memory if possible though it will cause the memory overhead to be less painful for the OS. When PunktDB.DAT validation is not used and a parameter value is to be written it has to be read first (read-before-write) if not already in memory. If this parameter is set to 0 ms, the parameter is only read once, not each time the parameter is written. This will significally improve performance for multiple writes. |
| CacheUpdateMin | 30000 ms | msecs that at least must elapse before the driver re-reads a single read parameter (altough request speed from Citect could be severely faster). This parameter should not be lowered unless an analysis is made of bus load. |
| CacheUpdateMax | 120000 ms | msecs that we at most will let the driver do other things than updating our parameter. If bus load is balanced, then the cached single read objects will be requested from the device using the CacheUpdateMin interval. If bus is fully loaded due to bad configuration or too many devices on a single gateway the update interval will be set to CacheUpdateMax |
| MaxScanListElements1 | 24 | Maximum number of parameters the driver will ask for in one packet. The devices are not capable of handle more than the default. |
| MaxScanListsPerUnit | 20 | Max number of scanlists each unit will be capable of handling. This number is also limited by the device memory. Available memory depends of device configuration. |
| MaxScanListNumber | 250 | The highest scanlist number the driver will use. The driver will always increase the scanlist number when creating a new scanlist to avoid conflicts with old – deleted - scanlists. Due to the queues nature of DNIP an scanlist update could arrive following a scanlist deletion. If the driver had re-used the deleted scanlist number if would have returned wrong values to Citect. |
| ScanListCacheLiveTime | 20000 ms | msecs we wait until the driver will delete a scanlist if Citect have not requested any parameter belonging to the specific scanlist. If the user switches between pages several scanlists may be created and they will not be deleted until this time has elapsed, even if the user returned to the main page. |
| ScanListFlushTime | 80 ms | When Citect send read DCBs to the driver, the driver will first of all queue them (if they not belong to a function block to be read as a complete block). When this time has elapsed, the driver will create a scanlist of the requested parameters. If more than MaxScanListElements is requested within ScanListFlushTime the driver will create more than one scanlist. If the number of read DCBs does not exceed ScanListTreshold the requested parameters are read as single reads. |
| ScanListTreshold | 2 | See above |
| ScanListInterval | 60000 ms | When scanlists are created, all parameter values are immediately sent back to the driver from the device. To ensure the device still is alive, and to ensure no values are lost, it will cyclically send a complete image of the parameter values using this interval, even If no values have changed. When any value is changed the device will immediately send an update to the driver (which will report it back to Citect). The hysteresis is device dependant. |
| ScanListIntervalTrend | 60000 ms | Specific for variables requested by the trend server (Trend.DBF) |
| ScanListIntervalAlarm | 60000 ms | Specific for variables requested by the alarm server (DigAlm.DBF) |
| ScanListStaleTime | 180000 ms | If no updates from the device arrives within this time, then the list is considered stale and will be removed. It should be at least double ScanListInterval time. |
| ForceOffLine |  | If specific devices are out of order they can be excluded from the initialising sequence. This will increase performance. Ex: 10:10,11:9-11:12,11:56-11:57,12:10 will set the devices in the specified interval (or as single devices) offline and no packets will be sent to them. |
| RedundantAddress |  | The address to the other I/O Server if the DNIP driver built in redundancy algorithm should be used. This parameter should not be set if normal Citect redundancy using different DHC addresses is to be used. The address must include portnumber, ex: ioserver2:12666 192.168.108.78:12567 The portnumber is automatically selected as the local server port for connection requests from our redundant counterpart. When a switchover to a new active server is made, the active server will remain active until a new condition requires a switchback. The switchover will be made when the active server no longer have contact to any device (determined per channel). If there is no address (or an invalid address) entered as RedundantAddress, no redundancy threads will be started. |
| RedundantConnectTimeout | 5000 ms | When an I/O Server is starting and the driver DLL (DNIP.DLL) is loaded for the first time (it will be reinitialized in a number of instances corresponding to the number of channels/ports) it will try to contact the other I/O Server DNIP.DLL redundancy server thread. This is the timeout for the first connection attempt, it has a separate timeout though it is important the driver have a connection to the other driver when Citect is trying to set devices online. |
| RedundantReconnectInterval | 10000 ms | If the first connection attempt fails (or the conneciton is lost for some reason), new connection attempts will be made using this interval. In real life the interval will be added to the normal TCP timeout algorithm (which can be up to two minutes). |
| RedundantKeepAliveInterval | 1000 ms | When a connection is made, the supervisor thread will send keepalive packets to the remote server thread for two reasons: first to ensure we still can send (the second I/O Server is still alive), second to indicate to the remote server thread we still are alive. Though both I/O Server have both client and server threads there will be two connections, one in each direction. |
| RedundantKeepAliveTimeout | 10000 ms | When the local server thread haven’t received a keepalive packet within this interval, it will assume the client connection is lost and shutdown the socket. This will set the thread in a listen state to be ready for a new connection attempt. |
| RedundantRequestTimeout | 2000 ms | When Citect is trying to set a device online, the DNIP driver will request the device online status from the other I/O Servers DNIP.DLL. If it does not answer within this timeout, the device is considered to be offline on the remote side, hence the local driver will try to set it online. |
| MinScanListNumber | 0 | To prevent mixups of scanlists, they should have different ranges for the primary and secondary I/O Server (ex 0-99, 100-199) if the driver built in redundancy is used. |
| MaxScanListNumber | 250 | See above |
| RedundantAllowSplitChannels | 0 | The redundant determination process will try to keep all devices on a channel (port) communicating through one I/O Server, but setting this parameter to 1 will let both I/O Servers have equal right to initialise any device (still only one I/O Server will communicate to a single device). |
| WriteDigitalAsFF | 0 | If set to 1, it will cause the driver to use the byte value 0xff instead of 0x01 when writing digitals. |
| PacketNumberRange | 17-255 | Range for packet numbers. Could be separated for each redundant counterpart, ex IOServer1 have 17-127, IOServer2 have 128-255. This is not necessary for the driver in a redundant configuration, but could ease up when tracking down problems. |

1 The parameter could be device specific, i.e. set in a section named:

[DNIP/DANDUC_010_010]

where DNIP is default and DANDUC_010_010 is the primary I/O Device name (even if entered in the standby IOServer Citect.INI)

The device specific setting will override if the parameter is entered also in the [DNIP] section.

## Driver Specific Errors

| Driver Error Code | Mapped to (Generic Error label) | Meaning of Error Code |
| --- | --- | --- |

## Driver Error Help

The following entries should be included in the Citect ProtErr.DBF spec file.

| PROTOCOL | MASK | ERROR | MESSAGE | REFERENCE | ACTION | COMMENT |
| --- | --- | --- | --- | --- | --- | --- |

## Debug Messages

Shows the outgoing/incoming data packets in hex. If error report level is set to ERROR the driver will report errors, i.e. if any point is asked for that is not configured in the device. The format is of Undefined Point: 013:001/AI2.7, which means device 013:001, Analog Input 2, parameter 7 (this is the same address that is entered in the tag variable database, AI02.7 or AI2.7.

## Stats Special Counters

| Number | Label | Purpose/Meaning of this counter |
| --- | --- | --- |
| 0 | DCB Requests | Number of DCB requests (accumulated) |
| 1 | Tx packet acks | Number of sent packet acknowledgements |
| 2 | Rx packet acks | Number of received packet acknowledgements |
| 3 | Tx DNIP packets | Total number of sent DNIP packets |
| 4 | Rx DNIP packets | Total number of received DNIP packets |
| 5 | Resent DNIP packets | Resents packets caused by timeout. |
| 6 | Unrequested packets | Packets received that was not asked for. |
| 7 | Inbuffer max | Maximum used bytes in the input buffer for the CPU service function (before they have been handled by the packet receive routine) |
| 8 | Cache hits | Number of DCB requests served by the cache |
| 9 | Cache hit rate (%) | The hit rate (Cache hits / DCB Requests x 100). |
| 10 | List Cache objects | Number of allocated cache objects associated with a scanlist (is calculated each second) |
| 11 | Single Cache objects | Number of allocated cache objects not associated with a scanlist (is calculated each second). This is single read cache objects. |
| 12 | Cache allocs | Total number of cache allocations. |
| 13 | Active ScanLists | Number of scanlists downloaded into the devices for this channel. |
| 1 | ScanList allocs | Number of scanlists we have allocated since last stats reset/restart |
| 14 | Phys. read time (ms) | Physical read time (round-trip time) for the last request. |
| 15 | Alarm Events | Number of alarm events. More or less alarms may have been indicated to Citect than viewed here, though they may be scanned through scanlists. |
| 16 | n/a |  |
| 17 | n/a |  |
| 18 | n/a |  |
| 19 | n/a |  |

## Hints and Tips

Be careful when entering tags. If any tags is created that has an invalid address it will cause up to 24 tags to not return any value at all due to the nature of the DNIP protocol. The erronous tag could be hard to find.

# Basic Testing

## Introduction

The programmer will perform a minimum level of testing which is outlined here.

A sample Project is available which can be used as a starting point for the programmers test Project. When the programmer has completed basic testing and debugging this Project should by backed up and supplied to the Citect Testing department.

## Procedure

The following are points should be covered by basic testing.

- On startup the IO Device comes online without errors.

- OK

- The driver supports IO Devices of addresses as documented in the specification.

- OK

- The driver reports the IO Device offline when the IO Device is a) powered down, b) disconnected.

- OK

- The driver will re-establish communication with the IO Device after a) power cycle, b) disconnection/ reconnection.

- OK.

- Confirm that retries (if supported) and error reporting operate correctly.

- OK (Statistics report)

- The driver reads all the device data types documented as readable in this specification.

- OK

- The driver writes to all the device data types documented as write-able in this specification.

- OK

- The  driver reads and writes all data formats supported by the protocol, ie DIGITAL, INT, LONG, REAL, BCD, LONG_BCD.

- OK

- Test the limit of the IO Devices request size, this should be done for at least DIGITAL and an INT data formats.

- Not applicable to this driver.

- Let the driver run over night and check that no retries or other errors have occurred.

- OK

- If a multidrop or network protocol and if the hardware is available then the protocol should be tested with more than one IO Device connected.

– OK (11 devices tested)

# Performance Testing

## Introduction

Tests which give some indication of the drivers performance. The programmer needs to perform these tests since the results feed back into the Constants  structure and the PROTDIR.DBF.

## Calculating the Blocking Constant – Not applicable

Because this driver is a hybrid of the ‘Front-End-Back-End’ type, and due to the nature of the DNIP protocol, it does not support blocking of any kind. The reading from the device consume the same amount of time independant of the location and type of the data.

# References

## References

These references are attached/delivered as Word 6.0 Documentation files.

MKS001	Meddelelse Krav Specifikation – Danfoss DANBUSS®
MKS002	Meddelelse Krav Specifikation – DANDUC™
MKS003 	Meddelelse Krav Specifikation – Danfoss MPV