Citect for Windows

Driver Specification

Fidelix

- Driver version history

| Version | Date | Modified By | Details |
| --- | --- | --- | --- |
| 1.0.0.B1 | 2013-03-05 | Tomas Rook | Main development – no writes, no TimeTables |
| 1.0.0.B2 | 2013-03-26 | Tomas Rook | Writes implemented (still no TimeTables) |
| 1.0.0.0 | 2013-04-22 | Tomas Rook | TimeTables and Calendar implemented |
| 1.0.0.1 | 2013-10-22 | Tomas Rook | Temporary WriteToLogFile -> not released |
| 1.0.0.2 | 2013-10-25 | Tomas Rook | Increased max include 64 -> 256, changed memset in init, increased MaxChannel 64 -> 256 -> not released |
| 1.0.0.3 | 2015-03-30 | Tomas Rook | OID lookup changed to prevent variable mixup between include projects, new BuildVariableMap to work better in redundancy, PortFrom defaults to port 1235 and TCP. XTA/XVA range fixup (did not compile correct) |
| 1.0.0.4 | 2015-03-31 | Tomas Rook | Removed IOServer compare stuff, added debug for defined variables missing in the Fidelix device |

- Driver documentation version history

| Date | Modified By | Details |
| --- | --- | --- |
| 2013-03-05 | Tomas Rook | Preliminary |
| 2013-03-26 | Tomas Rook | Statistics and parameters updated |
| 2013-04-22 | Tomas Rook | Parameters and Fidelix.dbf updated |
| 2015-03-30 | Tomas Rook | Parameters and Fidelix.dbf updated |

Contents

1.	QA	5

1.1	Introduction	5

1.2	Procedure for generating a new driver	5

2.	Target Device(s) and Protocol	6

2.1	Introduction	6

2.2	Device Manufacturer	6

2.3	Device Definition	6

2.4	Communications Method	6

2.5	Communications/Hardware Configuration	6

2.6	Contacts	6

3.	Protocol Requirements	7

3.1	Introduction	7

3.2	Pointlist	7

3.3	OID vs Index based adressing	7

3.4	FIDELIX.DBF	8

3.5	Supported variables/parameters	9

3.6	Address examples (OID and Index lookup)	11

3.7	Time channel addressing	13

4.	User Interface	14

4.1	Introduction	14

4.2	Driver Name	14

4.3	Ports Form (TCPIP setup)	14

4.3.1	Baud Rate	14

4.3.2	Data Bits	14

4.3.3	Stop Bits	14

4.3.4	Parity	14

4.3.5	Special Opt	14

4.4	IO Devices Form	14

4.4.1	Protocol	14

4.4.2	Address	14

4.5	Pulldown lists Help	15

4.6	PROTDIR.DBF	15

4.7	Parameters and INI options	15

4.7.1	Standard Parameters	15

4.7.2	Driver Specific Parameters	15

4.8	Debug Messages	16

4.9	Stats Special Counters	17

4.10	Hints and Tips	17

5.	Basic Testing	18

5.1	Introduction	18

5.2	Procedure	18

6.	Performance Testing	20

6.1	Introduction	20

6.2	Calculating the Blocking Constant – Not applicable	20

7.	References	21

7.1	References	21

# QA

## Introduction

This document follows the development of the new driver. It serves as a functional specification, design specification and test specification.

## Procedure for generating a new driver

The following check list defines the QA steps for generating a new driver. This procedure must be followed for drivers to be integrated into Citect.

|  | Description | Person | Date |
| --- | --- | --- | --- |
| 1 | This specification document is written. | TR | 13.03.05 |
| 2 | Specification reviewed and accepted by R&D department. |  | n/a |
| 3 | Driver coded. | TR | 13.03.05 |
| 4 | Code and specification reviewed and accepted by R&D department. |  | n/a |
| 5 | Testing with connection project, and performance test. | TR | 13.03.05 |
| 6 | Driver integrated into Citect source and built. |  | n/a |
| 7 | Documentation is written (HLP or MVB files) |  | n/a |
|  | At this checkpoint coding is done and the driver is available as a beta. |  |  |
| 8a | Full testing is carried out. | TR | 13.04.23 |
| 8b | Performance testing is carried out. | TR | 13.04.23 |
| 8c | Specification and documentation updated from testing/performance tests | TR | 13.04.23 |
|  | At this checkpoint the testing is complete. |  |  |
| 9a | Review for completeness by developer, tester, documentor and R&D staff |  | n/a |
| 9b | Add driver to install disks |  | n/a |
| 9c | Add driver to protocols database |  | n/a |
| 9d | Support notified of new driver for training purposes |  | n/a |
| 10 | Sales notified of new driver |  | n/a |
|  | The driver is now finished. |  |  |

The hand over of a driver requires that all the above steps are completed and checked off.

# Target Device(s) and Protocol

## Introduction

This section defines the types of I/O Devices that are targeted by this driver.

## Device Manufacturer

Fidelix Sverige AB
Box 62
647 05 Åkers Styckebruk

## Device Definition

Different model of devices, ex FX-2025

## Communications Method

TCP/IP only.

## Communications/Hardware Configuration

The driver connects to the Fidelix devices using TCP/IP and subscribe for tag updates.

## Contacts

Driver Development	TroSoft AB, Tomas Rook	+46 8 532 57262
Project Management	Fidelix Svenska AB, Antero Engberg	+46 8 556 558 33

# Protocol Requirements

## Introduction

The driver is a classic front-end/back-end cached driver using OID for variable lookup. It is also capable of index based variable lookup which will allow use in ‘blackbox’ projects (2013-03-05 not yet tested)

Driver was developed using DDK 5.5 and Citect 6.10 SpA, and has been tested with Citect 7.30. Later OS’s will report driver is old an maybe not compatible. The driver will be recompiled for VS2010 when Citect release their new DDK.

## Pointlist

When the driver DLL has loaded and communication takes place it will first of all read the Fidelix version and compare with the stored pointlist version. If it differs (or the pointlist file does not exist) it will be read. The pointlist is stored in Citect’s data folder, where a new folder ‘Fidelix’ is created. The pointlist will be named as the I/O device in Citect communications folder, ex C:\Documents and Settings\All Users\Application Data\Citect\CitectSCADA 7.10\Data\fidelix2.dat. An alternative path could be used, se Parameters section.

## OID vs Index based adressing

Fidelix devices only support text based addressing. Citect compiler is however not capable of handling text based addressing methods, hence the driver make use of direct variable database (Variable.DBF) address lookups. When the driver DLL is loaded it will scan through all variable tag databases in both the start project and all include projects. The unique OID key for all Fidelix variables will be stored in memory together with the variable address field. When Citect wants to read some variable, it sends the OID to the driver which look in its variable lists and hopefully finds the variable address.

To force the driver reading the pointlist again (if device configuration has been changed), the virtual digital tag DEVICE.GETPOINTLIST could be set to TRUE. The pointlist will always be read at startup if it does not exist or the parameter ReadPointListAtStartup is set to 1. The driver will automatically try to read the version of the Fidelix program and reload the variable list if it is changed.

If the pointlist file is not updated when configuration changes some variables could be missing causing address range error.

In some cases this is a method that will not function properly, ex if the variable tag databases does not exist locally (BlackBox project). To allow for these configurations the driver also support index based lookups. To enable index based addressing, the parameter AllowBlackBox should be set to 1. When enabled, the driver DLL will also create a text based cross-reference index file and put in the same folder as the pointlist file. Here are some variables in index file C:\Documents and Settings\All Users\Application Data\Citect\CitectSCADA 7.10\Data\fidelix2.txt:

…
1343=S03_LB01_GQ4X-MIN_MV.Value

1344=S03_LB01_GQ4X-MIN_MV.ValueAuto
1345=S03_LB01_GQ4X-MIN_MV.LockState
1346=S03_LB01_GQ4X-MIN_MV.Text
1347=S03_LB01_GQ4X-MIN_MV.Page
1348=S03_LB01_GQ4X-MIN_MV.Unit
…

the file will be quite big because all variables are expanded with their parameters.

To access variable S03_LB01_GQ4X-MIN_MV.Text the index 1346 should be used.

If pointlist is reread, the driver will try to update the index file. It will never delete any variables, even if they are deleted from the Fidelix. New variables will be added using previously never used index numbers.

If index based lookup has been used, the index file(s) should never be deleted because the driver will create and enumerate a new file, and the index numbers may change causing severe work for the user.

It is important distributing also the index files if the project is moved.

## FIDELIX.DBF

| Template | Unit type | Raw type | Bit width | Read/ Write | Comment |
| --- | --- | --- | --- | --- | --- |
| DEVICE.GETPOINTLIST | 0x50000000 | 0 | 1 | R/W | Force pointlist reread |
| OTA:%K%#.TimeArray | 0x70000000 | 1 | 16 | R/W | Time array (72 int’s) |
| OVA:%K%#.ValueArray | 0x71000000 | 1 | 16 | R/W | Time value array (72 int’s) |
| XTA:%U%*256 | 0x20000000 | 1 | 16 | R/W | Time array (72 int’s) |
| XVA:%U%*256 | 0x21000000 | 1 | 16 | R/W | Time value array (72 int’s) |
| XD:%U%*256 | 0x30000000 | 0 | 1 | R/W | Digital value from Fidelix |
| XI:%U%*256 | 0x31000000 | 1 | 16 | R/W | Integer value from Fidelix |
| XR:%U%*256 | 0x32000000 | 2 | 32 | R/W | Real value from Fidelix |
| XL:%U%*256 | 0x34000000 | 4 | 32 | R/W | Long value from Fidelix |
| XS:%U%*256 | 0x37000000 | 7 | 1024 | R/W | String value from Fidelix |
| XB:%U%*256 | 0x38000000 | 8 | 8 | R/W | Byte value from Fidelix |
| OD:%J%K%! | 0x60000000 | 0 | 1 | R/W | Digital value from Fidelix |
| OI:%J%K%! | 0x61000000 | 1 | 16 | R/W | Integer value from Fidelix |
| OR:%J%K%! | 0x62000000 | 2 | 32 | R/W | Real value from Fidelix |
| OL:%J%K%! | 0x64000000 | 4 | 32 | R/W | Long value from Fidelix |
| OS:%J%K%! | 0x67000000 | 7 | 1024 | R/W | String value from Fidelix |
| OB:%J%K%! | 0x68000000 | 8 | 8 | R/W | Byte value from Fidelix |
| %U%*256 | 0x30000000 | 0 | 1 | R/W | Digital value from Fidelix |
| %U%*256 | 0x31000000 | 1 | 16 | R/W | Integer value from Fidelix |
| %U%*256 | 0x32000000 | 2 | 32 | R/W | Real value from Fidelix |
| %U%*256 | 0x34000000 | 4 | 32 | R/W | Long value from Fidelix |
| %U%*256 | 0x37000000 | 7 | 1024 | R/W | String value from Fidelix |
| %U%*256 | 0x38000000 | 8 | 8 | R/W | Byte value from Fidelix |
| %J%K%! | 0x60000000 | 0 | 1 | R/W | Digital value from Fidelix |
| %J%K%! | 0x61000000 | 1 | 16 | R/W | Integer value from Fidelix |
| %J%K%! | 0x62000000 | 2 | 32 | R/W | Real value from Fidelix |
| %J%K%! | 0x64000000 | 4 | 32 | R/W | Long value from Fidelix |
| %J%K%! | 0x67000000 | 7 | 1024 | R/W | String value from Fidelix |
| %J%K%! | 0x68000000 | 8 | 8 | R/W | Byte value from Fidelix |

The DEVICE.GETPOINTLIST template could be used to force the driver re-reading the pointlist. If set to 1 it will begin reading, when finished the driver will automatically reset it to 0.

Point description texts are not writable. If changed in device, a new pointlist must be retrieved for the texts to be updated.

## Supported variables/parameters

IN

Value
ValueAuto
LockState
Text
Page
StatusText

DO

Value
ValueAuto
LockState
Text
Page
StatusText

AI

Value
ValueAuto
LockState
Text
Page
Unit
Limit[1-8].Value
Limit[1-8].Manual
Limit[1-8].Text

AO

Value
ValueAuto
LockState
Text
Page
Unit

CT

Offset
Text
Lookup[1-15]in
Lookup[1-15]out

TT

Value
LockState
Text
TimeArray (array of 72 int's)
ValueArray (array of 72 int's)

AL

Value
ValueAuto
LockState
Acknowledged
Priority
Status
StatusText
AlarmGroup
AlarmNumber
AlarmStatus
Text

ST

Value[0-19]
Text[0-19]

CO

Text
Page
DaySetLockState
RunState
RunLockState
NightSetValue
NightPBand
ReturnLimitStart
ReturnLimitPBand
StatusText
DaySetValue
StagesUsed
Stage[0-5]Name
Stage[0-5]Value
Stage[0-5]PBand
Stage[0-5]LimitStart
Stage[0-5]LimitPBand
Stage[0-5]OutMin
Stage[0-5]OutMax
Stage[0-5]OffValue
PBand
ITime
DeadZone
SampleTime
SlowSpeedFactor

CALENDAR

Calendar[0-9]
Holiday[0-9]

## Address examples (OID and Index lookup)

Typical tag of Data Type Real using OID lookup. Address format here is same as in the Fidelix OPC server.

Typical tag of Data Type String using OID lookup, forced to data type String. Sometimes the Citect compiler is not able to determine the size of a variable (mostly strings) and will return bad data to the user. Prefixing the address with a specific data type solves this problem. The prefixes OD, OI, OR, OL, OS, OB are used with OID lookups.

String tag from Calendar, it contains semicolon separated dates, ex:

100913Fr03;101013Fr03;0000000000; 0000000000;….

Prefixing the address with a specific data type (OS) ensures variable is handled as a string internally in Citect.

Typical tag of Data Type String using index lookup, forced to data type String. Sometimes the Citect compiler is not able to determine the size of a variable (mostly strings) and will return bad data to the user. Prefixing the address with a specific data type solves this problem. The prefixes XD, XI, XR, XL, XS, XB are used with index lookups.

Typical tag of Data Type Real using index lookup.

## Time channel addressing

Time values are stored in two arrays, TimeArray and ValueArray containing timestamps (stored as integers 0000..2359 or 9999 for ‘not in use’) and its desired value.

The array(s) have 72 elements (3 start/stop values Monday..Friday, followed by 3 start/stop values for E1, E2, E3, HD, HA).

Time array (timestamps) example.

Ex from above TEST_LB01_TimeArray[24] would contain first start time for Friday.

TEST_LB01_ValueArray[24] would contain the first start value for Friday.

TEST_LB01_TimeArray[25] would contain the first stop value for Friday.

# User Interface

## Introduction

This section defines how the user will see the driver. This relates directly to how the Citect forms need to be filled out and any special INI options. For the kernel, the debug trace messages and the Stats.Special counters are documented.

## Driver Name

Fidelix

## Ports Form (TCPIP setup)

### Baud Rate

n/a

### Data Bits

n/a

### Stop Bits

n/a

### Parity

n/a

### Special Opt

-i	The destination server IP-address, ex –i192.168.123.10.

-p	The destination server IP-port, ex –1235.

-t	Use TCP/IP (default)

Neither RS-232 (COMX) nor UDP can be used.

## IO Devices Form

### Protocol

Fidelix

### Address

n/a

## Pulldown lists Help

The following entries should be included in the Citect Help.DBF spec file.

| TYPE | DATA | FILTER |
| --- | --- | --- |
| PROTOCOL | FIDELIX |  |

## PROTDIR.DBF

The following entries should be included in the Citect Protdir.DBF spec file.

| TAG | FILE | BIT_BLOCK | MAX_LENGTH | OPTIONS |
| --- | --- | --- | --- | --- |
| FIDELIX | FIDELIX | 16 | 2048 | 0x2000cf |

## Parameters and INI options

### Standard Parameters

Block	16		(Citect blocking is prohibited)
Delay	1	ms
MaxPending 	75
Polltime	0	ms
Timeout	10000	ms
Retry	0		(Sets the complete packet retries, should be 0)
WatchTime	30	s

### Driver Specific Parameters

All Fidelix specific parameters are located in the section ‘Fidelix’

| PARAMETER | DEFAULT | DESCRIPTION |
| --- | --- | --- |
| TimeOut | 10000 ms | Response timeout for the device (even partly received packets will reset the timout timer) |
| MaxPending | 75 | Number of DCBs the driver may handle simultanously. Actually the default is quite low for this driver, but Citect is not capable of handling an unlimited number of outstanding DCBs. This number must be multiplied by number of channels to get the total DCBs for Citect. |
| WatchTime | 30 s | When Citect send DCB requests to the driver, it have to respond within this time. This is also the cycle time for init and status requests for offline devices. |
| ConnectTimeout | 15000 ms | msecs before we consider the IP connection/reconnect has failed. The IP layer may have an unreasonable timeout up to 120 seconds. |
| TraceToLogFile | 0 | If set to 1, it will cause the driver to write debug data to the file Fidelix.log stored in Citect’s data folder. The file will only be created if debug in Kernel is used. No check is made to ensure disk is not filled by the log file. |
| TraceOptions | 0 | Options for trace (may be bit-weighted togheter): 1 – Trace found I/O devices in DBF’s 2 – Trace variables found in DBF’s (will also trace I/O devices) |
| TraceLimit | 40 | Limits the number of bytes presented in Kernel when using debug-command. |
| IgnoreStartupErrors | 0 | If set to 1, irregularities in the variable database will not be reported. However, the parameters will be set as bad values if requested by Citect. Default is that the driver reports any potential problem at startup time using a messagebox. The messagebox will however block the startup sequence. |
| AllowBlackbox | 0 | If set to 1 the driver will create and also update an text based index file used for index variable lookup. |
| RequestInterval | 50 ms | Each request cycle, the driver will scan through internal queues for work to do (create packets, update statistics, cleanup memory, return new values from cache etc). Performance is linear to this time. If cache is fully updated the driver will return an average of MaxPending / RequestTime values per second (default 75 / .050 = 1500 values). Min value is 10 msecs. Timer granularity is depending of OS. |
| ReadPointListAtStartup | 0 | If set to 1, it will force the driver DLL to reread the pointlist when Citect is starting, even if the pointlist file already exists. |
| RestartInterval | 5000 | When device times out, it will wait this small amount of time before trying to initiate communications again. The Fidelix device close sockets very fast sometimes if no communication takes place, hence this time should not be very long. |
| UpdateInterval | 2000 | Number of msecs between each request for updated tags |
| AltRunPath | [CTEDIT]RUN | Alternative Run path, is used to find the top project. |
| AltUserPath | [CTEDIT]USER | Alternative User path. Is used by OID lookup mechanisms to find the Master.DBF file. |
| AltDataPath | [CTEDIT]DATA | Alternative Data path. Is used to determine where to store pointlist and index files. If set to the comms project path also index files will be backed up. |
| TimeTableWriteDelay | 500 | Delay time before TimeTables are written. This prevents multiple writes to device when same tables is updated. |

## Debug Messages

Shows the outgoing/incoming data packets. Header in verbose format and data/value in hex.

## Stats Special Counters

| Number | Label | Purpose/Meaning of this counter |
| --- | --- | --- |
| 0 | DCB Requests | Total number of driver requests |
| 1 | Tx bytes | Transmitted bytes |
| 2 | Rx bytes | Received bytes |
| 3 | Tx packets | Transmitted packets |
| 4 | Rx packets | Received packets |
| 5 | GetVersions | Number of GetVersion commands (issued at startup/reconnect) |
| 6 | GetPointlists | GetPointList commands (number of point list rereads) |
| 7 | GetChgPoints | GetChangedPoint commands (number of variable updates) |
| 8 | SetPoints | SetPoint commands (number of variable writes) |
| 9 | Updated vars | Number of updated variables (read) |
| 10 | n/a |  |
| 11 | n/a |  |
| 12 | n/a |  |
| 13 | n/a |  |
| 14 | n/a |  |
| 15 | n/a |  |
| 16 | n/a |  |
| 17 | n/a |  |
| 18 | n/a |  |
| 19 | n/a |  |

## Hints and Tips

None for now

# Basic Testing

## Introduction

The programmer will perform a minimum level of testing which is outlined here.

A sample Project is available which can be used as a starting point for the programmers test Project. When the programmer has completed basic testing and debugging this Project should by backed up and supplied to the Citect Testing department.

## Procedure

The following are points should be covered by basic testing.

- On startup the IO Device comes online without errors.

- Ok

- The driver supports IO Devices of addresses as documented in the specification.

- Ok

- The driver reports the IO Device offline when the IO Device is a) powered down, b) disconnected.

- Ok

- The driver will re-establish communication with the IO Device after a) power cycle, b) disconnection/ reconnection.

- Ok

- Confirm that retries (if supported) and error reporting operate correctly.

- Ok (Statistics report)

- The driver reads all the device data types documented as readable in this specification.

- Ok

- The driver writes to all the device data types documented as write-able in this specification.

- Ok

- The  driver reads and writes all data formats supported by the protocol, ie DIGITAL, INT, LONG, REAL, STRING.

- Ok

- Test the limit of the IO Devices request size, this should be done for at least DIGITAL and an INT data formats.

- Not applicable to this driver.

- Let the driver run over night and check that no retries or other errors have occurred.

- Ok

- If a multidrop or network protocol and if the hardware is available then the protocol should be tested with more than one IO Device connected.

– Ok

# Performance Testing

## Introduction

Tests which give some indication of the drivers performance. The programmer needs to perform these tests since the results feed back into the Constants  structure and the PROTDIR.DBF.

## Calculating the Blocking Constant – Not applicable

Because this driver is a hybrid of the ‘Front-End-Back-End’ type, and due to the nature of the Fidelix protocol, it does not support blocking of any kind

# References

## References

n/a.